Page 1 of 2

Documentation File for 240V to 110V Autotransformer

Date : 19-May-87

This text describes the addition of an autotransformer to the

Tandon PC Hard Disk [SIC] boxes to allow them to run from 240V.

Transformer Specifications :

Primary		240V Centre Tapped "PRIM"

60 Ohm total resistance

Secondaries	11V Centre Tapped "LT"

2 Ohm total resistance

28V Centre Tapped "HT"

2 Ohm total resistance

Rating		50VA Approx

H      H      H      H       H       H       H

----------------------------------------------------------------

|       LT    PRIM    HT    N/C     PRIM     HT      LT        |

|                                                              |

|                                                              |

|        LT C/T                                                |

|       ----------------------------------------------         |

|       |      ----------------------- HT C/T        |         |

|       |      |      ------------------------ *     |         |

|       |      |      |     N/C      |       |       |         |

----------------------------------------------------------------

H      H      H      H       H       H       H

* Note the winding marked "*" is the Primary Centre Tap

Wiring as Autotransformer

A ---------------------------------------

|                           |  --------

|    --------------         ---| FAN  |

|    |            | *       ---| 110V |

-----|PRIM    PRIM|--       |  --------    ----------

|        C/T | |----------------------| 110 V  |

|            | |                      | EQUIP  |

-----|PRIM        |--                      |        |

|    |            |                     ---|        |

|    --------------                     |  ----------

|                                       |

N ---------------------------------------------------

Page 2 of 2

Notes :

1. Wiring the fan (or fans) between 240V and 110V reduces the load on the

transformer (increases the output capability).

2. The other transformer windings can be used, but at the expense of

VA rating as an autotransformer.

3. The boxes come with 2A fuses. This should be reduced to 0.75A.

4. The core gets hot (due to eddy currents), even if there is no load

on the transformer. The maximum load is determined by winding resistive

heating.

5. Make sure your transformer mounting is safe, and insulate all live

terminals. The life you save may be your own.

6. The 110V transformer is capable of more than the autotransformer

can deliver. You could try two in parallel if need be.

7. Mounting the transformer is YOUR problem.

8. Check ALL your wiring (and the continuity of the Transformer)

with a meter. Never trust documentation.

Maximum load calculations:

Max load for a transformer can be defined as the load at which

the output voltage drops by 10%.

10% drop on 110V = 11V

11V across 30 Ohms (half winding) = 0.367A

Output current = 2 windings at .376A ea = 0.73A

Output VA = 110 * .73 = 81 VA

Transformer dissipation at Max Load = 2 * (11 * .367) = 8W

You can push it further if you fan-cool it, but burning transformers smell

AWFUL (and can set fire to things).